## choosing dosing nozzle
Nozzle # | Nozzle 1 (small) | Nozzle 2-5 (medium) | Nozzle 6 (large) |  | Gas type, conditions, and measurement range
Dosing rate (volumetric) | 0.5 | 3 | 15 | mℓ/s | Gas | SF6: 146.06 |  | Decimal | .
Dosing rate (gravimetric) | 10929.3879 | 65576.3274 | 327881.6372 | mg/h | Molecular mass | 146.06 | g/mol
Air flow rate [m³/h] | Concentration [mg/m³] |  |  |  | Temperature | 293.15 | K
10 | 1092.9388 | 6557.6327 | 32788.1637 |  | Pressure | 101325 | Pa
15 | 728.6259 | 4371.7552 | 21858.7758 |  | Density | 6.0719 | kg/m³ = mg/mℓ
22.5 | 485.7506 | 2914.5034 | 14572.5172 |  | Gas detection limit | 0.006 | ppmv
33.75 | 323.8337 | 1943.0023 | 9715.0115 |  | Sample integration time | 20 | seconds
50.625 | 215.8891 | 1295.3349 | 6476.6743 |  | Detection limit factor | 0.5 | -
75.9375 | 143.9261 | 863.5566 | 4317.7829 |  | Calibration type | normal | (1-point calibration)
113.9062 | 95.9507 | 575.7044 | 2878.5219 |  | Linear measurement range (dynamic range):
170.8594 | 63.9672 | 383.8029 | 1919.0146 |  | Minimum | 0.003 | ppmv | 0.018216 | mg/m³
256.2891 | 42.6448 | 255.8686 | 1279.3431 |  | Max (1-point calibration) | 60 | ppmv | 364.3129 | mg/m³
384.4336 | 28.4298 | 170.5791 | 852.8954 |  | Note: Norwegian Arctic University (UiT) recomments measurement range 5 - 25 ppmv for SF6
576.6504 | 18.9532 | 113.7194 | 568.5969
864.9756 | 12.6355 | 75.8129 | 379.0646
1297.4634 | 8.4237 | 50.5419 | 252.7097
1946.1951 | 5.6158 | 33.6946 | 168.4732
2919.2926 | 3.7438 | 22.4631 | 112.3154
4378.9389 | 2.4959 | 14.9754 | 74.877
6568.4084 | 1.6639 | 9.9836 | 49.918
9852.6125 | 1.1093 | 6.6557 | 33.2786
14778.9188 | 0.73953 | 4.4372 | 22.1858
22168.3782 | 0.49302 | 2.9581 | 14.7905
33252.5673 | 0.32868 | 1.9721 | 9.8603
Air flow rate [m³/h] | Concentration [ppmv]
10 | #N/A | #N/A | #N/A
15 | #N/A | #N/A | #N/A
22.5 | #N/A | #N/A | #N/A
33.75 | 53.3333 | #N/A | #N/A
50.625 | 35.5556 | #N/A | #N/A
75.9375 | 23.7037 | #N/A | #N/A
113.9062 | 15.8025 | #N/A | #N/A
170.8594 | 10.535 | #N/A | #N/A
256.2891 | 7.0233 | 42.1399 | #N/A
384.4336 | 4.6822 | 28.0933 | #N/A
576.6504 | 3.1215 | 18.7289 | #N/A
864.9756 | 2.081 | 12.4859 | #N/A
1297.4634 | 1.3873 | 8.3239 | 41.6197
1946.1951 | 0.92488 | 5.5493 | 27.7464
2919.2926 | 0.61659 | 3.6995 | 18.4976
4378.9389 | 0.41106 | 2.4664 | 12.3318
6568.4084 | 0.27404 | 1.6442 | 8.2212
9852.6125 | 0.18269 | 1.0962 | 5.4808
14778.9188 | 0.1218 | 0.73077 | 3.6539
22168.3782 | 0.081197 | 0.48718 | 2.4359
33252.5673 | 0.054131 | 0.32479 | 1.6239
Note on H6: density [kg/m³ ≡ mg/mℓ] = (P·M)/(R·T) where P = pressure [Pa] M = molar mass [kg/mol] = 0.001·[g/mol] R = universal gas constant 8.314472 [J/K·mol ≡ m³·Pa/K·mol] T = temperature [K] Note: EPA's definition of STP is 101325 Pa & 25°C
Note on H7: From Innova "Gas detection limits" spreadsheet or wall chart, for specific gas and filter
Note on H8: Chosen setting in Innova PC-logger software. 5 seconds is default.
Note on H10: What kind of calibration has been done for this particular gas? Normal = calibration with one concentration Accurate = calibration with two different concentrations

## gas cylinder
Gas |  | SF6: 146.06
Molecular mass |  | 146.06 | g/mol
Cylinder volume |  | 10.3 | liters (stamped on cylinder)
Cylinder tare weight |  | 15.4 | kg empty weight (stamped on cylinder)
Weight of attached valve (if any) |  | 0 | kg
Temperature |  | 20 | °C
Density at STP |  | 6.0719 | kg/m³
Dosing nozzle on Innova multiplexer |  | 1 (small)
Dosing rate |  | 0.5 | mℓ/s | 5e-07 | m³/s | 0.0018 | m³/h | 3.0359e-06 | kg/s | 3.0359 | mg/s
Wanted concentration at STP |  | 10 | mg/m³ | RT/P
|  | 1.6469 | ppmv <= (i.e. volume fraction), normal definition for ventilation / atmospheric sciences
|  | 8.305 | ppmw <= (i.e. mass fraction) used for other branches of science (advantage is that it is independent of changes in temperature & pressure)
Price full cylinder |  | 12114 | cost/cylinder (annual rent is in addition)
| Estimation by pressure: | Estimation by weight:
Cylinder weight |  | 16.3 | kg with gas
Net weight of gas | 1.2345 | 0.9 | kg
Gas quantity (n) | 8.4517 | 6.1619 | mol
PV = nRT = | 20600 | 15018.8191 | J or m³Pa
Pressure in cylinder | 20 | 14.5814 | bar
Pressure in cylinder | 2000 | 1458.1378 | kPa
Pressure in cylinder | 20.3874 | 14.8638 | kp/cm², kilopounds per cm²
Volume at STP (1atm; °C above) | 0.20331 | 0.14822 | m³
Dosing time available from cylinder | 112.9479 | 82.3468 | hours | ← 31% discrepancy between the two estimates
Price per hour (assuming full) | 107.253 | 147.1096 | kr/hour (assuming full cylinder)
Note on C20: Ideal gas law: PV=nRT P = pressure [Pa] v = volume [m3] n = # of moles R = gas constant [J/(K·mol) = m³·Pa/(K·mol)] T = temperature [K]
Note on B23: Ideal gas law: PV=nRT P = pressure [Pa] v = volume [m3] n = # of moles R = gas constant [J/(K·mol) = m³·Pa/(K·mol)] T = temperature [K]
Note on C23: Ideal gas law: PV=nRT P = pressure [Pa] v = volume [m3] n = # of moles R = gas constant [J/(K·mol) = m³·Pa/(K·mol)] T = temperature [K]